Hands-On Scenarios

PLC Tabletop Training Program · v1.0 · April 2026

Bench exercises — instructor-staged faults. Timing and success criteria as listed.

Scenario 1: Tripped Area Scanner — Machine Won't Start

Objective: Diagnose why the machine will not enter auto cycle. Identify the fault, clear the condition, reset the scanner, and restore cycle-ready state.

Time limit: 15 minutes

Setup (instructor)

Instructor places a small object inside the area scanner's protective zone, holding the OSSD output low. The HMI shows 'Safety Circuit Fault.'

Steps

• Read HMI alarm code and note the associated tag name

• Open PLC software and go online

• Find the safety circuit rung — confirm the scanner input tag is FALSE

• Physically inspect the scanner's detection zone

• Remove the obstruction from the protective zone

• Verify the scanner OSSD output returns to TRUE in the PLC

• Clear the fault on the HMI and verify the machine enters Ready state

Success criteria

Participant correctly identifies the scanner input tag, removes obstruction, resets fault, and machine enters ready state within 15 minutes.

Scenario 2: Network/IP Issue — Cannot Connect to PLC

Objective: Diagnose why the laptop cannot connect to the Omron PLC. Correct the IP configuration and establish a successful online connection.

Time limit: 10 minutes

Setup (instructor)

Instructor sets the laptop Ethernet adapter IP to the wrong subnet (e.g., 10.0.0.50 when PLC is 192.168.1.100). Sysmac Studio shows 'Connection Failed.'

Steps

• Open Command Prompt and run ipconfig — note the current IP address

• Ping the PLC IP address — confirm no response

• Open Network Connections, identify the correct Ethernet adapter

• Change the IP address to the same subnet as the PLC (e.g., 192.168.1.50)

• Ping again — confirm successful response

• Open Sysmac Studio and connect to the PLC

Success criteria

Participant correctly identifies and corrects the IP address, pings successfully, and connects to the PLC within 10 minutes.

Scenario 3: Proximity Sensor Signal Not Reaching PLC

Objective: A conveyor sequence is stuck because a proximity sensor signal is not reaching the PLC. Diagnose whether the fault is in the sensor, wiring, or PLC input channel.

Time limit: 20 minutes

Setup (instructor)

Instructor disconnects a wire at the proximity sensor output terminal block (or loosens a wire nut). The PLC tag reads 0 even when a metal target is present at the sensor.

Steps

• Identify the sensor tag name from the HMI alarm or I/O dashboard

• Go online in PLC software — confirm the input tag is 0

• Trigger the sensor manually — confirm sensor LED turns on (sensor works)

• Check the I/O module channel LED — if dark, the signal isn't reaching the module

• Measure voltage at the I/O module terminal with a multimeter

• Trace the wiring back from the module to the sensor terminal block

• Find and fix the disconnected wire

• Verify the PLC tag reads 1 when the sensor is triggered

Success criteria

Participant uses sensor LED, multimeter, and PLC tag monitor to isolate the wiring fault and restore the signal within 20 minutes.

Scenario 4: Logic Fault — Output Not Energizing

Objective: An output (light tower or relay) is not energizing. Trace the ladder rung to identify which input condition is preventing the output.

Time limit: 20 minutes

Setup (instructor)

Instructor changes a timer preset to an extremely long value (e.g., 30,000ms instead of 3,000ms). The downstream output never energizes because the timer DN bit never activates in normal observation time.

Steps

• Open PLC software, go online, navigate to the affected program block

• Find the output coil that should be energizing

• Work left to right on the rung — identify which contact is not passing power

• Find the timer contact (DN bit) that is blocking — note the timer is still counting

• Check the timer preset value — recognize 30,000ms is abnormally long

• Compare to documentation or expected value (should be 3,000ms)

• Correct the timer preset and confirm the output energizes

Success criteria

Participant traces the rung to the timer, identifies the incorrect preset, corrects it, and confirms output energizes within 20 minutes.

Scenario 5: Component Replacement — Faulty Push Button

Objective: A push button has failed. Replace it, rewire correctly, and verify the PLC receives the signal.

Time limit: 25 minutes

Setup (instructor)

Instructor provides a push button with a disconnected or swapped wire. The HMI shows the associated input is not responding to button presses.

Steps

• Identify the push button channel from the wiring diagram

• Confirm the input tag is not toggling using PLC Tag Monitor

• Remove the old button (disconnect wiring, note wire labels)

• Install the replacement button in the correct location

• Reconnect wiring to the correct terminals matching the wiring diagram

• Test the button — confirm the PLC input tag toggles with each press

• Verify the associated function works in the machine sequence

Success criteria

Participant correctly replaces the push button, makes proper wiring connections, and verifies PLC signal within 25 minutes. Wiring is neat and terminal screws are torqued.